## BOQ
SCHEDULE OF QUANTITIES FOR THE NAINITAL BANK LTD. ,DIT AT SECTOR 62, NOIDA .
| DESCRIPTION | QTY. | UNIT | RATE in Fig | Rates in words | AMOUNT
1 | PARTITIONS
1.01 | Providing and fiixing Full Height Wooden Partitions, 3"thk. Made up of 2"x2" Aluminium framework @ 2'-0" ' c/c bothways with 8mm + 3mm sandwiched plywood skinning on boith sides with 1.00 mm thk laminate on both the sides over the plywood skinning, with necessary Pedilite SH adhesive, screws and bolts, etc; and with necessary grooves. Unexposed surfaces shall be treated with antitermite wood preservatives before covering up complete as per architects directions and approval. The frames to be taken above the False ceiling and fastened to the RC ceiling. Mode of Measurement shall be on the exposed are only I.e.upto false ceiling. | 2700 | Sft.
1.02 | Low Height Wooden Partitions, 3"thk. Made up of 2"x2" Aluminium framework @ 2'-0" ' c/c bothways with 8mm plywood skinning on boith sides and 1.00 mm thk laminate finish on both the sides over the plywood skinning with necessary Pedilite SH adhesive, screws and bolts, etc; including providing Duco painted top trim with MDF of size: 3" x 3/4" and necessary grooves etc. as directed. Unexposed surfaces shall be treated with antitermite wood preservatives before covering up complete as per directions and approval. | 125 | Sft.
1.03 | Full Height Glazed Partition- Providing and fixing Full Height Glazed Partitions of 3"thk. Made up of 2"x2" Aluminium framework @ 2'-0" ' c/c bothways with 8mm + 3mm sandwiched plywood skinning on boith sides with necessary Pedilite SH adhesive, screws and bolts, etc; & above 12mm thk float glass with aproved quality and pattern frosted film, as per design Glass panel to be fixed with 19 X 32.5 mm beachwood beading alround. Glass to be butt jointed and edges to be ground/machine polished to get a flush joint complete as directed and sealed with silicone sealent. Framework of partition is to be fixed to RC ceiling for support. | 450 | Sft.
1.04 | Glazed window in Partition Providing and fixing Glazing in Partions with Aluminium frame/beading 20mm thick on both sides with 8mm thick clear float glass with frosted film as per design as shown in the detailed drawings. All woodwork to be finished with Melamine Polish. | 90 | sft
1.05 | Laminated Wall Panelling: Providing & Fixing Plywood panelling with 2" x 1" Aluminium framework at 2'-0" c/c fixed over the existing wall/ partition and 12mm plywood boarding to and finishing using 1.0mm laminate of , as directed and the fixed to the fixed to the wall/ partition with necessary pedilite SH adhesive, screws etc. including providing grooves and skirting as per drawing. | 1050 | Sft.
1.06 | ACP Wall Panelling: Providing & Fixing ACP sheet panelling with 2 1/2" x 1 1/2" Aluminium framework at 2'-0" c/c fixed over the existing wall/ partitions | 325 | Sft.
TOTAL I
2 | DOORS FRAME & SHUTTERS.
2.01 | Glass Door: Providing and Fixing Glazed Door of 12mm thk. Toughened glass with etching/frosted film. Each shutter to have brush stainless steel handle, Dorma Floor Spring and locking arrangements as per detailed drawings.
| Type ED1- 3'6" x 7' 0" | 2 | Nos.
| Type D1- 3' 0" x 7' 0" | 3 | Nos.
2.02 | Laminated Door : Providing and fixing 38mm thick Solid Core Flush shutter made out of 35mm flush shutter with TW lipping alround finished with 1.5 mm laminate on both sides, with grooves as shown with Vision Panel of 6mm glass with frosted film and fixed with beechwood beading. Shutter edges to be duco painted with matching color. All the doors shall be 10mm. Above the finished floor level as directed. Complete as per drawing inclcuding hardware and door closers.
| Type D2- 3' 0" x 7' 0" | 6 | Nos.
2.03 | Laminated Door: Providing and fixing 38mm thick Solid Core Flush shutter out of 35mm flush shutter with TW lipping alround finished with 1.0 mm laminate on both sides, with grooves as shown. shutter edges to be duco painted with matching color. All the doors shall be 10mm. Above the finished floor level as directed. Complete as per drawing inclcuding hardware and door closers
| Type D3- 3' 0" x7' 0" | 1 | Nos.
| Type D4- 2' 6" x7' 0" | 1 | Nos.
2.04 | Laminated Partly Glazed Door: Providing and fixing 38mm thick Solid Core partly glazed Flush shutter out of 35mm flush shutter with TW lipping alround finished with 1.0 mm laminate on both sides, with 10mm thk clear float glass fixed with 12 x 20 mm BW beading to the shutter and with grooves as shown. Shutter edges to be duco painted with matching color. All the doors shall be 10mm. Above the finished floor level as directed. Complete as per drawing inclcuding hardware and door closers
| Type D5- 2' 6" x7' 0" | 1 | Nos.
2.05 | Providing and Fixing of Steam Beach Door Frame in section: 4" x 2.5" for
a | Type D2 - 3' 0" x 7' 0" | 6 | Nos.
b | Type D4 - 2' 6" x 7' 0" | 4 | Nos.
TOTAL II
3 | LOOSE AND FIXED FURNITURE Note: Only post form table top shall be used in all tables, side units etc.
3.01 | Providing and Fabricating Laminated CMD Table with laminated side credenza including pedestal units, modular keyboard tray etc. size 7'6'x 3'6" | 0 | Nos.
3.02 | Providing and Fabricating Laminated Table with with laminated side credenza pdestal units, modular keyboard etc in size 5'6"x 3'0" | 5 | Nos.
3.02a | Providing and Fabricating Laminated officer Table with pedestal units with laminated side credenza, modular keyboard etc in size 5'0"x 2'6" | 5 | Nos.
3.02b | Providing and Fabricating Laminated Lecture officer Table with pedestal units with laminated side credenza, modular keyboard etc in size 4'0"x 2'6" | 0 | Nos.
3.03 | Providing and Fabricating work Table of size 5 '0" x 2'6" with 2'x 2 '6"' vertical wooden supports for every 4 1/2' intervals . For every 4 1/2 ' length one modular key board tray shall be provided with Laminated pedastal / Drawer units having 2 drawer with lock & key complete... The internal portions shall be duly polished . Rate including of fittings,one pedastal / drawer unit for each work station and soft & writing board has to be fixed to the wall/partition for the entire length. | 48 | Seat
3.06 | Laminated Running Counter: Proving 2' 6" Deep Laminated Server Room Counter with 1.5mm laminate and BW beading and supports at 4' 0" centres as shown in the drawings. | 12 | Rft.
3.07 | CONFERENCE Table of Top size 16'0"X4'0" Made out of teak wood frame of approved design and etc with polish etc all complete as per the bank approved desing with 10 mm thick Plate Glass top. | 1 | EACH
3.08 | Lunch Table of Top size 8'0"X3'0" Made out of teak wood frame of approved design and etc with polish etc all complete as per the bank approved desing with laminate top. | 8 | EACH
3.09 | SOFA : Providing and placing in position sofa made of 75 x 75 mm hardwood section and 19 mm BWP ply bottom (anti termite treatment), springs, jute cloth, coir, cotton HDF, loose foam, seat with 75mm thick and back with 50 mm thick, upholstery @ Rs. 150=00 per meter shade as approved by Architect all complete as per drawing. The item should be finished as per specification and approval in all respects. (2 No. – 3 seater ) | 6 | seat
TOTAL III
4 | STORAGES
4.01 | Full Ht. Laminated Storage - Fabricating and fixing 1' 6" deep storage unit constructed out of 19mm. Thk comm.ply sides and 19mm thick shutters-side hung with 1mm laminate, 12mm.thk BW lipped comm.ply bottom. Outside shall be with 1mm laminate and Inside of the units shall be finished with 0.6 mm laminate all over. All exposed wooden surfaces to be melamine polished with necessary SS hardware like Spring box hinges, Handles, Al. tower bolt and Godrej multipurpose lock complete as directed. | 285 | Sft.
4.02 | Medium Ht. Laminated Storage- Fabricating and fixing 1' 6" deep storage unit of height 4' 0" to 5' 6" Storage units to be constructed out of 19mm thk plywood top and sides with 1.5mm laminate for top and 1 mm laminate for vertical surface and shutters-side hung with 12mm.thk BW lipped comm.ply. Outside shall be finished with 1mm laminate and all inside of the units shall be finished with 0.6 mm laminate all over. All exposed wooden surfaces to be melamine polished with necessary SS hardware like Spring box hings, Handles, A1. Tower bolt and Godrej multipurpose lock complete as directed. | 125 | Sft.
4.03 | Low Ht. Laminated Storage- Fabricating and fixing 1' 6" deep storage unit of height 2' 6" Storage units to be constructed out of 19mm. Thk plywood top and sides with 1.5mm laminate for top and 1mm laminate for vertical surfaces and shutters-side hung with 12mm. Thk BW lipped comm.ply. Outside shall be finished with 1mm laminate and all Inside of the units shall be finished with 0.8 mm laminate. All exposed wooden surfaces to be melamine polished with necessary SS hardware like Spring box hings, Handles, A1. Tower bolt and Godrej multipurpose locxk complete as directed. | 325 | Sft.
4.04 | Overhead. Laminated Storage- Fabricating and fixing 1' 6" deep storage unit of height 1' 9" Storage units to be constructed out of 19mm. Thk plywood top and sides with 1.5mm laminate for top and 1mm laminate for vertical surfaces and shutters-side hung with 12mm. Thk BW lipped comm.ply. Outside shall be finished with 1mm laminate and all Inside of the units shall be finished with 0.8 mm laminate. All exposed wooden surfaces to be melamine polished with necessary SS hardware like Spring box hings, Handles, A1. Tower bolt and Godrej multipurpose locxk complete as directed. | 18 | Sft.
TOTAL IV
5 | FALSE CEILING WORKS
5.01 | Providing & Installing Mineral Fibre Ceiling System comprising high humidity/fire resistant ceiling panels/Tiles, 15mm thick, Arstrong Contrast Linear, Microlook BE or approved Equivalent in exposed grid system Trulock (Silhoutte grid) or equivalent with 24 mm wide main and Cross T-sections,flange of white colour, as approved. The mainrunners (T.sections) shall be spaced at 1200 mm c/c. the last hangernot to be more than 450mm from adjacent wall. Flush fitting 1200 mm long fross tees to be interlocked between main runner at 600 mm centers to form 600mm x 600mm modules. Perimeter trim to be wall angle or channel white colour secured to walls @ 450 mm centers. Complete. Cost to include for cutouts for light fixtures, A/C grills, trap doors etc., as per drgs . The cost of no of tiles/panels not used in the places of grills, etc; shall be deducted from the total amount. | 3450 | Sft.
5.02 | Providing and fixing 12.5 mm. Thk. Plain Gypsum Board False Ceiling including verticals, boxing, float, etc; on 24 gauge G.I grame work shich includes providing & fixing G.I. operimeter channels 0.55 mm thk 20mm x 30 mm, web size 27mm along perimeter of ceiling,screw fixed to brick wall/partition complete as per specification of India Gypsum Ltd. Rate to include for providing cutous for grills, diffusers light fixtures, etc; and strengethening the edges with additional channels if necessary as directed. | 900 | Sft.
TOTAL V
6 | FLOORINGS
6.01 | Vinyl Flooring : Providing and laying 2 mm thick vinyl flooring of Krishna Vinyl or approved equivalent make laid as per manufacturers specifications. Payment will be made on the actual area laid.in UPS Room | 45 | Sft.
TOTAL VI
7 | MISCELLANEOUS WORKS
7.01 | Providing and applying Spectrum Textured Paint of “Spectrum” make or equievelent of “spray bubble coat compact” shade as per drawings/ directions & manufactur’s specifications including two coats of emulsion painting over the texture | 2800 | Sft.
7.02 | Providing and painting of wall with 3 coats of Acryilic Emulsion paint of approved shade & make on wall/plywood/gypboard etc., including all necessary surface preparation. The wall shall be cleaned, filled & applied with 2 coats of primer so as to achieve an even surface to apply paint. | 650 | Sft.
7.03 | Providing and Painting of wall with 3 coats of Enamel paint of approved shade & make etc., including all necessary surface preparation. The applying surface shall be cleaned, filled & applied with 2 coats of primer so as achieve an even surface to apply paint. | 900 | Sft.
7.04 | Providing and fixing Soft Board with 6mm. Thk. Commercial ply as backing and 12 mm thk. Soft board with fabric finishing, complete as per drawings. Paneling to have B.W moulded framework out of 25 x 19 mm finished with melamine polish. | 190 | Sft.
7.05 | Providing and fixing openable Trapdoor Shutters for airconditioning indoor units in 19mm marine ply finished with approved laminate on both sides with concealed ss hinges (Union SJS 304, 100mm), on wood framework of 85mm x 60mm. The framework shall be secured to the ceiling with proper vertical ms / teakwood sections. All the exposed and internal surfaces shall be finished with enamel paint to match the ceiling colour. L- end trapdoor lack (Godrej/ union make) complete. | 28 | Sft.
7.07 | Roller Blinds : Supply & Installation of Chain Operated Roller Blinds of “Grorich Horivert” make, with powder coated Aluminium Head rail and Aluminium Fabric pipe with insert spleen groove for easy insertion of fabric with spleen. Metal load bar to be provided at the bottom of the shade screen for holding the shades in posiotion against wind, etc;. The operating mechanism inserted at the ends of the headrail to consist of two control units. Active spring tensioned mechanism with chainsprocket and acetal operating chain and passive end control with chain sprocket and acetal operating chain and passive end control with pressure release lever-adjustor to remove the shade for maintenance, including necessary brackets,clamps, bottom rail with end caps, etc; complete as per manufacturer’s specifications. The blind fabric shall be from “Solitis 99-2055” in Horivert series. | 825 | Sft.
7.08 | Mirror: Providing and fixing 6mm thick mirror " Modifloat or equivalent" with 6mm marine plywood becking and bw lipping 1/2" x 1/4" as shown in the drawing | 22 | Sft.
7.09 | Stool: Providing and fixing Wooden step stool in the store room as per design | 4 | Nos.
7.1 | Aluminium Windows: Providing and fixing Aluminium Windows powder coated with sliding windows glass panels as per design | rate only | Sft.
7.11 | Safety Grill: Providing and fixing Safety MS 12mm squre rod grill as per design for the external windows with red oxide paint | rate only | Sft.
7.12 | POP Punning: Providing and applying POP punning on walls in plumb level of average 1/2" thk. | 2800 | Sft.
7.13 | Pelmet : Providing and fixing Pelmet in plywood of 8" x 6" near the windows for the blinds | 145 | rft
7.14 | Shutter Boxing : Providing and fixing Marine plywood boxing for the rolling shutters with shutters in plywood on hinges | 350 | Sft.
7.15 | Providing and Fixing of Birla 3 mm frosted film | 250 | sft
TOTAL VII
8 | CIVIL WORKS:
8.01 | Providing and constructing Brick masonry 230 mm and above in superstructure including pillars at all levels and heights, with approved quality well burnt table moulded bricks of minimum crushing strength 50 kgs./sqcm i CM 1:6 proportion including the cost of all materials, labour, soaking bricks, staging, platform, curing, cost of building in holdfasts, providing holes etc. complete | 125 | Cft.
8.02 | Providing and constructing Brickwork in partitions 115mm thk. with approved quality well burnt table moulded bricks of minimum crushing strength 50Kgs/Sqcm in CM 1:4 proportion for walls upto 115 mm thickness at all levels and heights including cost of providing fabricating and placing in position 2 nos of 6mm dia steel bars at 4th course held together by 6mm stirrups at 150 mm c/c. the cost to include all materials, labour, soaking bricks, staging platform, curing, cost of building in holdfasts providing holes, etc complete. | 275 | Sft.
8.03 | Plastering surfaces of walls, beams, columns, chajjas, etc: with CM 1:4,20 mm with sponge finish at all levels and heights, including preparing the surface, adequate curing, staging etc; complete. The cost to include all materials and labour, screen and washing sand if necessary cleaning the floor, windows of splashes, providing grooves etc; for internal walls. | 500 | Sft.
8.04 | Water Proof plastering: Proving plaster 20mm thick in CM 1:3 with approved water proofing compound such as Conplast prolapin 4211c or equivalent for walls, sunken slabs and floors with neat cement smooth finish including coving in the corners and cost of all leads lifts scaffolding, sieving and finishing the surface to the required level, line and plumb at all level, curing, etc, complete. | 22 | Sft.
8.05 | Providing and laying RCC Lintels/beams of 1:2:4 grade using 20mm downsiize aggregate including necessary centring and shuttering staging, compacting the conrete, curing and deshuttering, | 0 | Cft.
8.06 | Providing and laying Vitrified Tile Flooring with glazed finish vitrified tiles of size 600 x 600 mm, laid in pattern as per design with adhesive from Roff Chemicals or laticrete or approved equivalent with 3mm joints and providing PVC spacers and joint finished with joint fillers from Latricrete to match the shade of the tile to the architects satisfaction. The rate to include laying, curing and covering the floor with PVC sheet and POP and removing and cleaning after completion as directed. (Marbonite Perlato- 2'-0" x 2'-0" Basic price of tile Rs. 95/-sft) | 4250 | Sft.
8.07 | Providing and Laying Vitrified Tile Skirting 150mm high with vitrified homogenous tiles to walls and partitions. | 325 | Rft.
8.8 | Providing and laying Ceramic Tile Flooring with tiles of size 300 x 300, 400 x 400 in floo9ring laid in pattern as per design, in cement mortar 1:6 or with adhesive from Roff chemicals or laticrete with joints finished jointing compound to match the shade of the tile to the achitects satisfaction. (Basic Price of tile Rs. 35/sft) | 80 | Sft.
8.11 | Providing Glazed Ceramic Tile Dadoing with tiles of 200 x 300/200 x 200 mm size of approved make over CM 1:3,15mm thick including pointing with approved quality Roff or Laticrete sealant laid in proper line and level including curing, cleaning and acid washing (Basic Price of Tile Rs. 35/Sft) | 325 | Sft.
8.12 | Polished Granite Flooring: Providing and laying Polished Granite flooring with 20mm thk. Slabs in flooring laid in pattern as per design in cement sand mortar 1:6 with joints finished jointing compound to match the shade of the tile to the architects satisfaction.(Basic Rate of the Slab Rs. 150/-sft.) | 345 | Sft.
8.13 | Granite Counter: Providing and constructing Pantry /Toilet counter of 2'-0" deep in granite top with half round moulding | 4 | Rft.
8.14 | Polished Granite Skirting: Providing and laying Polished Granite Skirting 4" high with 20mm thk. Slabs in cement mortar 1:4 with joints finished jointing compound to match the shade of the tile to the architects satisfaction.(Basic Rate of the Slab Rs. 150/-sft.) | 0 | Rft.
8.15 | Polished Granite Cladding: Providing and laying Polished Granite Cladding with 20mm thk. Slabs in cement mortar 1:4 with joints finished jointing compound to match the shade of the tile to the architects satisfaction.(Basic Rate of the Slab Rs. 150/-sft.) size 5" wide. | 275 | Rft.
8.16 | PCC 1:4:8 : Providing and laying PCC 1:4:8 below foundation, footing and floor with one part of cement four parts of approved river sand and eight parts of 40mm and down metal by volume including the cost of all materials, labour compacting, consolidating, etc. complete | 12 | Cft.
8.17 | Brick Bat Coba : Providing and laying Brick Bat coba of 4" thk. For the toilet including the cost of all materials, labour compacting, consolidating , etc. complete | rate only | Sft.
8.18 | Complete Plumbing piping works forToilet/ Pantry with Supreme Heavy Duty PVC pipe | 3 | LS
Sanitary Ware of Parryware/ Hindware
8.19 | Wash Basin under counter with angle cock & bib cock | 6 | Nos.
8.2 | Wall mounted WC with cistern and paper holder, tap | 3 | Nos.
8.21 | Urinal long body with angle cock & accessories | 4 | Nos.
8.22 | SS Sink with sink cock | 1 | Nos.
8.23 | Dismantling existing brickwork, blockwork, lintel, beams, slabs, etc. | 1 | LS
8.24 | providing and Fixing of the Rolling shutter | 345 | Sft.
TOTAL VIII
SUPPLY AND INSTALLATION OF LT PANELS
1 | PANEL FABRICATION DETAILS:
Supply, Installation, Testing and Commissioning of 3 Phase, 4 wire, 415 V, 0.8 P.F, 50 Hz. panels. The fabrication shall be made with 14SWG cold rolled sheet with M/c pressing. The surface shall be rigorously treated for derusting in 7tank process with dephosphating and painting with at least 2 coats of approved paint.
The panel shall be totally enclosed metal clad type with double gasketting with rubber/resin lining. The panelshall be off white painted inside and shall be having cont-rol directory pasted inside the panel. The panel shall be mounted on existing trench and shall have cable entry provision from the top and bottom with suitable alley as the case may be.The panel shall be tested for the same KA rating of the
relevant highest rating ACB / MCCB. All components shall be
from ISO-9001 companies and shall have relevant IS/IEC approvals
without fail. (Fabrication, drawing and list of components and panel
detail shall be got approved by consultants before fabrication).
The panel shall be fully interlocked as required.
The panel shall include baseframe channel support.
(The Single Line Diagram and enclosed brief scheme may
closely be followed).
Note: 1. The Panel shall be fully as per the requirement of
Electrical Inspectorate/ EB authorities.
2. Auxilliary contactor to be provided along with auto-
manual switch where ever required.
3. All Breakers both Incoming & Outgoing shall have
LED 'ON / OFF / TRIP' indications without fail.
4. 125 A Change over
5. ACBs earthing shall be carried out with Cu. Bus.
6. For Capacitors earthing shall be provided.
7. Ventilators shall be provided for Panels with 2500A & above rated bus bars.
8. Cu bus earthing shall be provided for all panels.
9. All ACBs shall confirm IS 13947-1/IEC 947-1 for general rules & IS 13947-2/IEC 947-2 for Circuit breakers.with shutter assembly & door seating frame.
10. SAFETY CERTIFICATE FOR THE PANELS SHALL BE
PRODUCED FROM CEIG.
11. All AC feeders will have time delays.
12. SAFETY CERTIFICATE FOR THE PANELS SHALL BE
PRODUCED FROM CEIG.
13. All ACBs / MCCBs shall be microprocessor based only.
14. All test certificates must be provided immediately after commissioning.
15.Any panel if more than 1.5m width should be made in parts
each part not exceeding 1.5m
16. The current density for ALU busbars shall be 0.75-0.8 only.
17. The current density for CU busbars shall be 1.0 only.
18. All UPS outgoing panels shall have neutral busbars double
the size of phase.
19. All MCCB's shall have setting from (40or50)-100%.
20. All Lighting / RP and Lift panels shall have ELR for incomer of Prok. Dvs. Make.
1 | FLOOR DISTRIBUTION PANEL
INCOMER :
1 No. CT operated 3 phase Energy Meter,.
1 No., 125 Amps, 25 KA TPN MCCB with ELR.
RYB indicator - 1 Set
AC Voltmeter with selector switch.
Ammeter with selector switch.
BUS - 200A. Alu TP + N + E
OUTGOINGS:
5 Nos. 63A TPN MCB.
3 Nos. 32A TPN MCB.
| Supply | 1 | No.
| Installation | 1 | No.
2 | UPS O/G DB
INCOMER :
1 No. 63A DP ELCB
BUS - 100A. Alu TP +2N + E
OUTGOINGS:
2 Nos. 32A TPN MCBs.
| Supply | 1 | No.
| Installation | 1 | No.
3 | Supply & instalation of 40 A TPN MCB with out door type IP-55 enclosure near AC Units
| Supply | 2 | Nos
| Installation | 2 | Nos
4 | Supply & instalation of 40 A TPN MCB with enclosure
| Supply | 2 | Nos
| Installation | 2 | Nos
TOTAL PART - A
PART - B - LT CABLE WORK
1 | Supply, Instalaltion, Testing & Commissioning of XLPE insulated sheathed steel tape armoured Aluminium UG cable with pvc outer sheathing 1.1 KV class .
The cable shall be either laid on existing cable trays or in existing trench.
The cable shall be tied with nylon ties on the cable tray and a overlapping 25x3mm GI strip shall be fixed to the cable tray. The cost of the nylon tie and overlapping GI strip shall be included in the cost of installation.
(Not to include the cost of cable trays/trench).
Armoured Aluminium Cable:
1.1 | 3.5 Core, 70 Sqmm cable.
From Main panel to floor panel .
| Supply | 65 | Mtr
| Installation | 65 | Mtr
1.2 | 4 C , 10 Sqmm cable.
a. From panel to AC DB
| Supply | 55 | Mtr
| Installation | 55 | Mtr
1.3 | 4 C , 16 Sqmm cable.
a. From Floor panel to RP DB / LTG. DB
| Supply | 55 | Mtr
| Installation | 55 | Mtr
2 | COPPER FLEXIBLE CABLE
2.1 | 1 C , 16 Sqmm cable.
a. From Floor panel to UPS-1
| Supply | 90 | Mtr
| Installation | 90 | Mtr
3 | Supply, Installation, Testing & Commissioning of End terminations for following cables using double compression tinned glands with Copper lugs using hydraulic crimping tools complete.
Aluminium cables:
3.1 | 3.5 Core, 70 Sqmm
| Supply | 2 | Nos.
| Installation | 2 | Nos.
3.2 | 4 Core, 10 Sqmm
| Supply | 2 | Nos.
| Installation | 2 | Nos.
3.3 | 4 Core, 6 Sqmm
| Supply | 2 | Nos.
| Installation | 2 | Nos.
4 | Copper cable - Single compression
4.1 | 1C x 16sqmm
| Supply | 2 | Nos.
| Installation | 2 | Nos.
TOTAL PART - B
PART - C : INTERNAL ELECTRICAL WORKS
1 | FINAL DISTRIBUTION BOARDS.
Supply, Installation, Testing and Commissioning of all MCB Phase Segregated Distribution Boards (9KA) made out of 16SWG MS sheet steel enclosure hinged MS cover/over flanged cover with cutouts for cutouts for operating the MCB knobs and comprising of phase busbars, neutrals and earth bus with tapped holes, bakelite phase barriors, pvc insulator shoes for incoming wire etc complete. DBs shall be mounted by grouting in to the wall/angle to brick wall as required.
DBs shall be suitable for single phase loads. Or DBs shall
be mounted on suitable M.S. angle and supporting flat.
DBs shall include termination lugs etc., all complete. As per
Electrical Inspectorate requirement.
(Note: 1. Local fabrication not permitted. Only factory made boxes
shall be installed and all MCBs shall be with 9 KA rating.
2. All UPS DB MCB shall be 'D' curve only)
1.1 | Lighting DB - LDB - 3 Phase 4 Way:
Incoming: 1 No. 63A TPN MCB.
Outgoings: 12 Nos. 10A SP MCB.
| Supply | 1 | Nos
| Installation | 1 | Nos
1.2 | RAW POWER DB - PDB - 3 Phase 4 Way:
Incoming: 1 No. 63A TPN MCB.
Outgoings: 12 Nos. 10/20A SP MCB.
| Supply | 1 | Nos
| Installation | 1 | Nos
1.3 | UPS DB - UDB - 3 Phase 4 Way :
3 Phase & 1 Phase Combined Distribution Board.
Incoming: 1 No. 63A TPN MCB.
Outgoings: 3 Nos. 40A DP MCB.
Outgoings: 12 Nos. 10/20A SP MCB.
| Supply | 1 | Nos
| Installation | 1 | Nos
1.4 | SERVER UPS DB - 1 Phase 12 Way:.
Incoming: 1 No. 40A DP MCB.
Outgoings: 12 Nos. 10/20A SP MCB.
| Supply | 1 | Nos
| Installation | 1 | Nos
1.5 | EMERGENCY LIGHTING DB - 1 Phase 4 Way:.
Incoming: 1 No. 40A DP MCB.
Outgoings: 4 Nos. 10/20A SP MCB.
| Supply | 1 | Nos
| Installation | 1 | Nos
2 | INTERNAL WIRING
Supply, Installation, Testing and Commissioning of point
wiring using (3 x 1.5) Sqmm 1100V grade stranded FRLS wires of approved make drawn in 25/19mm dia 2mm thick Rigid PVC conduit of approved make including all conduit accessories such as bends, junction boxes etc., complete. The wiring shall be done in complete looping in system. The switches used shall be moulded fixed in factory made integral GI box units with clear earthing facility.
The wiring shall be complete with ceiling roses, switches and all consumables.
The switches shall be of Anchor Roma - Tressa make only.
2.1 | PRIMARY LIGHT POINT
I. Primary light point means wiring from first switch control to the first light out let.
II. Not to include the incoming lighting circuit from MCB-DB to switch.
III. But to include the sub circuit if it is drawn from adjacent switch box.
IV. For drops from the ceiling flexible conduit shall be included.
| Supply | 80 | Pts
| Installation | 80 | Pts
2.2 | SECONDARY LIGHT POINT
I. Secondary light point means extention of light out let only from existing Primary point to be controlled by the existing switch of Primary point only.
II. For drops from the ceiling flexible conduit shall be included.
| Supply | 75 | Pts
| Installation | 75 | Pts
2.3 | To wiring as in item no. 2.00 using (2Rx 2.5+1.5) sqmm pvc insulated FRLS wire drawn in 19mm dia 2mm thick PVC conduit as lighting circuit, being recond from the distribution board to first light control switch.
(Looping will not be paid separately for next primary point)
| Supply | 800 | Mtr
| Installation | 800 | Mtr
2.4 | Supply & Installation of 6/16A 5 pin socket with SP switch without
indicator in appropriate make factory made GI boxes.
(Excluding circuit) - For Raw power.
| Supply | 32 | Nos.
| Installation | 32 | Nos.
2.5 | Supply & Installation of 5 A 3 pin switch socket
excluding boxes. - Excluding circuit - for Raw Power .
1 socket controlled by one switch with indicator.
| Supply | 45 | Nos.
| Installation | 45 | Nos.
2.6 | Supply & Installation of 2 Nos. 5A 3 pin socket with 15A
SP switch with indicator - (Excluding circuit) - for UPS.
| Supply | 28 | Set
| Installation | 28 | Set
2.7 | Supply & Installation of 2R x 4sqmm + 1R of 2.5sqmm PVC insulated
Copper wire for UPS / RP circuit
| Supply | 900 | Mtr
| Installation | 900 | Mtr
2.8 | Supply & Installation of 25mm dia 2mm thick rigid pvc conduit
excluding wiring with clamps, bends, suspensions etc.
For Data, UPS, Telephone and raw power conduiting.
| Supply | 700 | Mtr
| Installation | 700 | Mtr
2.9 | Supply & Installation of metal conduits to be used in flooring
excluding wiring with clamps, bends, suspensions etc.
For Data, UPS, Telephone and raw power conduiting.
| Supply | 75 | Mtr
| Installation | 75 | Mtr
2.1 | Supply & Installation of 25mm dia re-inforced flexible conduit
with coupling.
| Supply | 55 | Mtr
| Installation | 55 | Mtr
2.11 | Supply & Installation of 32mm dia 2mm thick rigid pvc conduit
excluding wiring with clamps, bends, suspensions etc.
For burglar alarm system conduiting.
| Supply | 165 | Mtr
| Installation | 165 | Mtr
2.12 | SITC of 3 Module switch box for data telephone | 18 | Nos
2.13 | Supply & Installation of 20A, Single phase, industrial type metal clad socket with
16A SP MCB enclosure in Server room.
| Supply | 4 | Nos.
| Installation | 4 | Nos.
2.14 | Exhaust fan point with 5A socket
| Supply | 6 | Nos.
| Installation | 6 | Nos.
3 | JUNCTION BOX
3.1 | Supply & Installation of 14 SWG GI 450x450x50mm floor junction box with cover to match with item no.4.00 above including co-ordination with other agencies for embedding in floor.
| Supply | 12 | Nos.
| Installation | 12 | Nos.
3.2 | Supply & Installation of 14 SWG GI 300x300x50mm floor junction box with cover to match with item no. 4.00 above including co-ordination with other agencies for embedding in floor.
| Supply | 2 | Nos.
| Installation | 2 | Nos.
TOTAL PART - C
PART - D : SUPPLY & INSTALLATION OF LIGHT FIXTURES
1 | Supply & Installation of light fixtures complete with lamps, starter,
ballast etc., complete. The rate shall include all mounting
accessories like angles, fasteners, supports, chain, adjustable hooks,
grip bolts and nuts etc., complete.
2 | Supply, fixing, testing & commissioning of 2X2 24W with LED fixture with low power & high efficiency LED chips with Lumen output >100 lumens/watt for better heat management. New generation high efficiency translucent diffuser for good light quality & no LED spot visibility. Luminaire housing should be CRCA powder coated in white.CG make. The CCT of LED should be 5700 Deg Kelvin or more. Driver should have efficiency of more than 80% and power factor should be > 0.9 & surge protection min 2KVtype.LED should be LM80 tested & report to be produced for better relability of LEDs Model no LCTLR-36-CDL or Eq.
| a. S.I.T.C. Of 12 Watt 6000/6500 K Recessed/ Surface mounted LED Down Lighting Fixtures with fixing accessories. | 65 | Nos.
| b. S.I.T.C. 7/8 Watt 6000/6500 K LED Surface /Recessed mounted Down Lighting Fixtures with fixing accessories. | 45 | Nos.
| c. 20W LED (Cove) batten Lights of Polycab/Havels/Philips /Bajaj. Recommended Model: PCGLB VX 20 65 Polycab Intenso VX LED Batten 20W | 40 | Rmt
3 | Supply & Installation of 2 x 13 W CFL recess mounted down lighter
Make : Epson / Eqvt.
| Supply | 0 | Nos.
| Installation | 0 | Nos.
4 | Supply & Installation of Decorative Surface mounted wall / ceiling mounted circular luminaire with housing in reinforced thermoplastic and opal polycarbonate vandal resistant dffuser suitable for 1 x 18W CFL lamp.
Make : Epson / Eqvt.
| Supply | 45 | Nos.
| Installation | 45 | Nos.
5 | Supply & Installation of surface mounted 4ft. / 2 ft. patti type luminaire suitable for 1 x 36W FTL lamp
Make : Epson / Eqvt.
| Supply | 18 | Nos.
| Installation | 18 | Nos.
6 | Supply & Installation of pendent / surface mounted industrial Box type luminaire suitable for 1 x 36W FTL lamp.
Make : Epson / Eqvt.
| Supply | 12 | Nos.
| Installation | 12 | Nos.
7 | Supply & Installation of wall mounted mirror light luminaire with
switching.
Make : Epson / Eqvt.
| Supply | 6 | Nos.
| Installation | 6 | Nos.
Supply, Installation & testing 400mm sweep wall fans (Model Swing Dezire Wall Fan/Crompton High Flo wall Fan) complete in all respect as per direction by architect or Co.
| Supply | 38 | Nos.
| Installation | 38 | Nos.
8 | Supply & Installation of 9" dia light duty exhasut fan
| Supply | 6 | Nos.
| Installation | 6 | Nos.
TOTAL PART - D
PART - E : EARTHING SYSTEM
1 | Supply and installation of pipe electrode earth station as per IS 3043 complete with 38mm dia 'B' Class GI pipe, GI watering funnel, 450mm x 450mm CI frame and heavy duty CI cover, 300mm brick masonary chamber etc., complete .
| Supply | 0 | Nos.
| Laying | 0 | Nos.
2 | Copper plate earth station as per IS 3043 complete with 600 x 600 x 3mm Copper (Tinned) plate B Class, GI pipe with watering funnel, 450 x 450 mm CI frame and heavy duty CI cover, 300mm brick masonary chamber etc., complete.
| Supply | 0 | Nos.
| Laying | 0 | Nos.
3 | Earth strips - GI / Copper.
3.1 | 25 x 3 mm GI flat
| Supply | 85 | Mtr
| Laying | 85 | Mtr
3.2 | Supply and laying of 1 Core 6 sqmm insulated copper wire for UPS .
socket earthing in 25mm dia pvc conduit.
| Supply | 25 | Mtr
| Laying | 25 | Mtr
3.3 | Supply and laying of 8 SWG GI wire .
| Supply | 35 | Mtr
| Laying | 35 | Mtr
TOTAL PART - E
BOQ FOR THE AC WORKS .
1 | 1.5 TR HWM Split Unit
Model (Economical model)
with Cordless remote
a | Unit Cost (Excise+Transport) | No. | 10
b | Installation | No. | 10
c | Outdoor Stand | No. | 10
d | Caging with Lock & Key facility | N0. | 10
Total
2 | Ref. Piping (Only single distance will be considered irrespective of number of circuits/compressors)
a | 2.0 TR HWM Split Unit | Mtr. | 245
Total
3 | Electrical cabling (Only single distance will be considered irrespective of number of circuits/compressors)
a | 2.0 TR HWM Split Unit | Mtr. | 245
Total
Cassette Type A/C Unit
4 | 3 TR Cassette Unit
a | Model (Economical model)
b | Corded / Cordless remote
c | Unit Cost (Excise+Transport) | No. | 8
d | Installation | No. | 8
e | Outdoor Stand | No. | 8
f | Caging with Lock & Key facility (optional) | N0. | 8
Total
5 | Ref. Piping (Only single distance will be considered irrespective of number of circuits/compressors)
a | 3.0 TR Cassette Unit | Mtr. | 185
6 | Electrical cabling (Only single distance will be considered irrespective of number of circuits/compressors)
a | 3.0 TR Cassette Unit | Mtr. | 185
Total
8 | MCBs
a | Weather proof MCB for units. | No. | 22
Total
13 | Drain Pipings
a | Drain piping - Hard PVC pipe (25 mm) with 12mm expanded polythene insulation | Mtr. | 225
Total
TOTAL FOR AC WORKS
PROPOSED DATA CABLING WORK
I | Data Cabling Works
a) | Supplying & Fixing of HCL CAT 6
10/100/1000 Mbps UTP Cable including the
| cost of laying the conduits and cable etc.complete | 2050 | Mts
b) | Supplying & Fixing of HCL CAT 6 Single
| information Outlet including the cost of | 75 | Nos
Punching & Fixing etc.complete
c) | Supplying & Fixing of HCL 24 Port 10/100
| Mbps Fast Ethernet Switch | 1 | Nos
d) | Supplying & Fixing of HCL CAT 24 Port
Patch Panel including punching & Fixing
| etc.complete | 1 | Nos
e) | Supplying & Fixing of HCL CAT 6 3 Feet
| Patch cord | 55 | Nos
f) | Supplying & Fixing of HCL Cat 6 7 Feet
| Patch cord (PC to IO) | 55 | Nos
g) | Supplying & Fixing of HCL 19" 9U Rack with
power manager & Cable Manager with fasteners
| including the cost of rack fixing etc.complete | 2 | Nos
Total Amount
ABSTRACT
SNO | DISCRIPTION |  |  |  |  | AMOUNT
1 | PARTITONS
2 | DOOR FRAMES AND SHUTTERS
3 | LOOSE AND FIXED FURNITURES
4 | STORAGES
5 | FALSE CEILINGS WORKS
6 | FLOORING WORKS
7 | MISC WORKS
8 | CIVIL WORKS
9 | ELETRCIAL PANELS
10 | CABLE WORKS
11 | INTERNAL ELECTRICAL WORKS
12 | ELECTRICAL FIXTURES
13 | EARTHING WORKS
14 | AC WORKS
15 | DATA CABLE WORKS
TOTAL
GRAND TOTAL