## SUMMARY
SUMMARY FOR NAINITAL BANK AT TALLITAL, NAINITAL
INTERIOR WORK
ELECTRICAL AND DATA WORKS
AC WORK
TOTAL
GST EXTRA AS APPLICABLE
NOTE:
1. UPS STAND BY NOT INCLUDED ABOVE ESTIMATE.

## INTERIOR
BOQ OF INTERIOR WORK FOR NAINITAL BANK AT TALLITAL, NAINITAL
INTERIOR WORK
SL.NO. | PARTICULARS | UNIT | QTY | RATE | AMOUNT
1 | FALSE CEILING ( Gypboard)
| Providing and fixing Gypsum false ceiling as per India Gypsum specification for ceiling with drops as per drawing including of providing and fixing G.I. Frame work as per specification of India gypsum at a distance of 2'0" c/c both ways complete with 12.5mm board and all necessary perimeter channels etc. No extra payment will be made for the cutting of light points , stain glass,cove lighting etc. The measurement will be taken in one level , rate should include the drops also, no extra amount will be paid for the drops. The joints to be properly mended with paper tapes and gypsum compound all complete. The rate should include the full completion of the ceiling. At the time of handing over the site all necessary repairing work to be considered if required. The work to be completed as per specification , approval of the Architect.No Drop or design(if any )will be considered as extra measurement it will be considered flat ceiling. | SFT | 790
1 ( B ) | FALSE CEILING (24"x24" GRID FALSE CEILING)
| 24"x24" Grid False Ceiling. Providing and Fixing False ceiling Grid using hot dipped Galvonised steel sections, exposed surface chemically cleaned capping pre-finished in baked polyster paint. Main tee of size 3000 x 32 x 24 mm at every 1200mm c/c maximum, 1200mm cross Tee of size 1200 x 27 x 24mm at every 600mm intervals and 600 mm cross Tee of size 600 x 25 x 24mm at every 1200mm max and 3000 x 19 x 19mm wall angle all around the wall to form grid size of 600mm x 600mm . The Main grid to be suspended to the MS frame with 2mm pre-straightened GI wire and GI adjustable clamp and Laying of fibre wool board having Fire rating of 60 min. as per BS 476/23 of 1987 , Noise reduction co-eff. ( NRC ) of 0.50, Light reflectance of 83%, Sound atteneuation of 32db, thermal conductivity of k=0.052 W/m, wt of 4kgs/mts and humidity resistance of RH-95 ,600x600mm x 12mm thick over the Grid. All as per the design and instructions Architects. | SFT | 850
2 | PARTITION.
Providing and fixing partition in position as per design with Providing and fitting wooden partitions with approved aluminium/ GI framework 2"X 1.5 " at the spacing 60MM X 60MM . Fitted 9MM commercial plywood on both side and Korean Mica sheet 1MM thick ( Colour - white and orange ) as per engineer / in -charge instructions. . The work to be completed as per design approval of the archiect.
A | PARTLY GLAZED PARTITION
(I) | PARTLY GLAZED FULL HT. PARTITION UP TO 8'- 6" HT. | SFT | 165
(ii) | PARTLY GLAZED LOW HT. PARTITION UP TO 7' - 0" HT | SFT | 125
(iii) | PARTLY GLAZED LOW HT. PARTITION UP TO 4'-6" HT | SFT | 145
B | BLOCKED PARTITION
(I) | FULL HT BLOOKED PARTITION UP TO 8'-6" | SFT | 165
(II) | FULL HT BLOOKED PARTITION UP TO 8'-6" at STRONG ROOM | SFT | 80
C | TOUGHEND GLASS PARTITION CASH COUNTER FRONT SIDE. | SFT | 40
3 | DOORS
Providing and fixing solid core 38 mm solid core flush door finished with lippings in all side with necessary door hinges , cylindrical locks(golden, Godrej) , door clouser, door stoppers, etc with a frame work of T.W./Beech wood size 75mm x 62.5mm with necessary hold fast fixed to the wall/partition. 1 mm laminate to be fixed on both sides duly finished,edges to be finished with wooden lippings.A wooden moulding size 1.5"x2/8" to be provided all along the periferi of the frame work in the both sides . All the wooden area to be duly polished as per specification of the Architect. In case of Partly glazed door 8 mm thk etched or plain glass with granular blasting/sand blasting as per design of the Architect to be fixed with necessary mouldings.
A | Partly glazed door
(I) | Partly glazed door with etching
| (7'x3') | No. | 1
| 7'x2'6" | No. | 0
(ii) | Partly glazed door with out etching & frosting
| 7'-0" x 2'6" cash counterr | Nos. | 2
| 7'X2'-6"/3'-0" ups room | Nos. | 0
B | Blocked door
(I) | Full ht. Blocked door.
| 2'-6"/3'-0"x7'-0" Store Room and passage door | Nos. | 5
| 7'x2'-6"/7'X2'-9" TOILET | Nos. | 0
| WICKET DOOR | Nos. | 0
C | MAIN Entrance Glazing with door
| Work will be complete incuding 6"x1.75" bottom and 5"x1.75" toprail wooden with 4" x 1.75" wooden frame steam beach section duly melamine finish, 12mm Thk. Toughened Glass , bank logo ,heavy duty door spring ,SS finish handle,lock godrej make. | SFT | 55
4 | TABLE
Providing and fixing tables made out of 19mm thk comm board of approved make cladded with 1.0 mm laminate( color with vertical grain) as per design in all visible areas. All the exposed edges to be covered with wooden lippings and mouldings duly malamine polish. The drawers to be made out of 19mm thk comm. board duly laminated in the front ,sides to be made out of 12mm comm. plyw and bottom to be made out of 6mm comm. ply and it should play in drawer sliding channels. The inside of the drawer and the table to be duly paint . A legrest to be provided duly paint made out of 3"x2" thk wooden section. A shutter to be made by 19mm comm. board cladded with1.0 mm laminate .The necessary locks handles to be provided in each drawers and shutters. 3" x 1/2" wooden skiritng to be provided in all visible areas duly polished. On top of the Branch managers table 8mm thk glass to be placed duly edge polished. The table should have key board tray and tea tray dulyfinished with 1.0 mm laminate. The necessary wire managers to be provided on the tables and provision for lights to be kept if required in the front of the table.
CPU trolly to be provided every where with a provision of castors to be provided .19mm comm. board & 12mm ply panel fix front side as per as per design including the raised level & perforations. The table have 12mm glass panel over wooden panel fix with SS Stud . All the exposed wooden areas to be duly malamine polished The work to be completed as per design and approval of the Architect
A | Branch Manager Table - 5'-6" X 2'-6" | No | 1
B | Officer table / cleark/p.officer 5'-0"X 2'-6" | Nos | 8
C | Running Counter | Rft | 12
D | Running counter for pantry with granite top | Rft | 1
5 | CASH COUNTER/TELLER COUNTER
Providing and fixing top, front & side of cash counter made out of 19mm comm. board as per design cladded with 1.0 mm thk. laminate & the edges to be finished with necessary wooden lippings, mouldings, etc. Special 6" drawer to be made for the cash with dividers of 12mm comm. ply. The front of the drawer made out of 19mm comm. board finished with 1.0 mm laminate, sides 12mm comm. ply and bottom to be made of 6mm comm. ply . The inside and sides of the drawer to be enamel painted .The drawers and shutters to be provided with necessary drawer sliding channels, hinges, locks etc. A leg rest to be provided made out of 3'x1.5" wooden section duly polished. Inside of the unit to be enamel painted in the matching tone.All visible areas on the edges to be coverd with wooden lippings, mouldings with natural polish. Wire manager, CPU trolly, keyboard tray, tea tray to be provided 3" x 1/2" wooden skiriting to be provided with natural polish in all visible areas.19mm thk Granite to be provided at counter top at 3' 8" lvl.
the work should be completed as per specification.
| as per specification.( 4' -6"to5'-0" Average Length) | NO. | 1
6 | Side and Back Unit
| Providing and fixing Side Unit/ Back unit made out of 19mm comm. board finished with 1.0mm laminate in all exposed areas . The drawers to be made out of 19mm comm. board in the front cladded with 1.0mm laminate. sides to be made out of 12mm comm.ply and bottom made out of 6mm comm ply duly painted in matching tone and it should play on drawer sliding channels . The shutters to be made out of 19mm comm. board and should play on drawer sliding castors on powder coated channels. The necessary locks , handles, etc to be provided . 3" x1/2 wooden skiritng to be provided duly polished as per matching tone all along the visible areas . Inside of the unit to be enamel painted in matching tone . All the exposed edeges of the boards/plywoods to be coverd with woden lippings/mouldings duly polished all complete.The work to be completed as per approval and specificaion of the Architect. | SFT | 125
7 | STORAGE
Providing and fixing Full height storage 400mm deep made out of 19mm bwp block board finished with 1.0mm laminate in all exposed areas . The drawers to be made out of 19mm BWP block board in the front cladded with 1.0mm laminate( color, vertical grain) .sides to be made out of 12mm plywood and bottom made out of 6mm plywood duly painted in matching tone and it should play on drawer sliding channels . The shutters to be made out of 19mm block board and should play on drawer sliding castors on powder coated channels. The necessary locks , handles, etc to be provided . 3" high laminated skirting to be fixed bottom side of the Storage. Inside of the unit to be enamel painted in matching tone . All the exposed edeges of the boards/plywoods to be coverd with wooden lippings/mouldings duly polished all complete.The work to be completed as per approval and specificaion of the Architect.
| Full/Low ht storage | SFT | 210
| Over Head Storage for pantry | SFT | 80
8 | Writing Ledge
| Providing and fixing writing ledge as per design made out 19mm comm. board with necessary grove patterns with 1.0mm laminate. 10mm thk machine polished glass to be provided on top of the writing ledge. Small boxes to be made out of 12mm comm. ply to be made on top of the writing ledge finished with 1.0 mm laminate, inside enamel painted .The work to be completed as per design and approval of the architect. | NO | 1
9 | POP
| Providing and applying pop on wall & column as per required and to give a smooth surface as per approval of the Architect. | SFT | 0
10 | PAINTING
a | Providing and applying Acrylic emulsion paints after removing the damaged plaster , replastering with 12mm thk cement morter finished with P.O.P to make the necessary smoothnes , reparing all damages . Then two coats of Primer of approved make to be applied finished with two or more coats of acrylic emulsion paints .The work to be completed as per approval and satisfaction of the Architect. | SFT | 0
b | TEXTURE PAINT
c | Providing , spraying and applying Texture paint as per approved shade as per approval of the architect. Bi colour texture paint will be used. The wall surface has to duly prepared by scraping , removing the damaged plaster and applying P.O.P to give a smooth surface as per approval of the Architect. | SFT | 600
| SYNTHETIC ENAMEL PAINT : FOR WINDOW GRILL, ROLLING SHUTTER & COLLAPSEABLE GATE | SFT | 400
11 | Cornice
| Providing and fixing wooden cornice moulding along the pheriferi wherever the walls/ partition meets the ceiling.Size 1 1/2" x 1 1/2" duly polished as per approval of the architect. | RFT | 0
12 | Suggestion Box
| Providing and fixing suggestion box as per drawing &approval of the architect | No | 1
13 | Cheque Deposit Box
| Providing and fixing cheque deposit box as per drawing &approval of the architect | No | 1
14 | Centre Table
| Providing centre table as per drawing &approval of the architect . | Nos | 1
15 | Side Table
| Providing centre table as per drawing &approval of the architect . (22"x22" avarage) | Nos | 2
16 | PILLAR and WALL PANELLING
a) | Providing and fitting wall paneling with Aluminum/GI section Size 1" X 1.5 " at the space 60MM X 60MM .Fitted 9MM thick Commercial plywood over the section fixed with Pinewood Stri 1MM thick ( Matching Colour - ) as per engineer/ in-charge instruction . The item is to be completed in all respects as per design,direction & approval of the architect. | SFT | 800
GRANITE CLADDIND(FRONT FASCED)
b) | Providing and fixing granite slabs with bi-colour pattern fixed with adhesive finish with jointing compound edges to be moulded polished all complite as per direction and approval of the Architect. | SFT | 65
17 | VERTICAL BLINDS
| Providing and fixing vertical blinds of 100mm thk of vista Lavour of approved shade and pattern. The rate shall include necessary scoch gurd treatment on both sides. The overlaping should be uniform and adequate.Necessary oparative arrangements,frames to be provided. The work to be completed as per specification and approval of the architect. | SFT | 50
18 | SOFT BOARD / NOTICE BOARD
| Providing and fixing soft board with necessary framework with 12mm commercial plywood on top jolly board to be fixed finished with fabric @Rs80 , with necessary mouldings duly polished along the periferi. | SFT | 20
19 | OUTER SHUTTTER BOX
| Overhead outside shutter box: p/f sal wood frame fixing of 12mm plywood with 1mm thk. Laminate finish and openable shutter for out side area | SFT | 400
20 | WALL DISPLAY BEHIND VISITOR AREA
| Structure made of 18mm plywood and gypsum board 6" depth boxing ,finish with1mm thk. laminate, splot light,flower vase, abstrac paintings as per drawings. | Sft | 50
21 | Mirror : Providing and suppyling mirror for strong room with drawer unit. | each | 1
22 | Paintings :- Hand made painting in glass frame (24"x18") | Nos | 2
23 | Planter box made by 19mm block board with 1mm thk. Laminate finish,Plants as per approval of the architect and provision to be fix it | Nos | 4
24 | Synthetic Door Mat
| Providing & fixing synthetic door mat 6mm thk. As per approval of the Architect. | Nos | 3
TOTAL
25 | Note:Tenderer should inspect the site and condition before quoting the rates of buy back item like table, storage, partition from old premises. | LS | 0
TOTAL

## ELECTRICAL WORK
BOQ OF ELECTRICAL WORKS FOR NAINITAL BANK TALLITAL, NAINITAL
SL. | PARTICULAR | Qty | Unit | Rate | Amount
1 | Supply,laying, connection &testing of light,
fan point, wiring by 2x1.5mmsq(2x3/.029) +
1x1mmsq PVC insulated copper flexiable wire
maintating the colour code as per direction in
PVC conduite of 20mm with ISI mark 1.5mm
thickness to conceal in wall partition mending
good the damage, complete with PVC circular
box, bend to be done as per drawaing
including 3 point ceiling rows wherever
required GI saddle to be used for fixing,
metal flexiable/PVC flexiable pipe may use
if requied in partition wall. All PVC pipes
should be with ISI mark. No joints will be
allowed inside pipe ,light, fan & plug point
complete with modular type switch plate &
MS box . Including the main circuite line 2x
2x2.5mmsq+1x1.5mmsq earth PVc insulated
Cu. Wire,maintaining the colour code. Circuite
line for lighting switch board ,6Amps plug
board are to be drawn from lighting DB to
Lighting board & plug point board, 6/16 Amps
plug point line are to be draw from power DB
amps plug to be & to 6/16 plug point board.
3Nos lighting board, 03 Nos.6Amps connected
from one circuite & one 02 Nos. 6/16 plug to
be connected from one circuite.
a) | Lighting point complete with modular type
switch, plate, M.S. conceal box.
| Point - 1 Light point control by 01 switch. | 22 | Nos
| Point - 2 Light point control by 01 switch. | 21 | Nos
| Point - 3 Light point control by 01 switch. | 10 | No.
b) | Exhust fan point same as item No. 1a complete with modualr type switch plate &MS conceal box & 3 pin ceiling rose. | 3 | Nos
c) | Ceiling fan point controlled by one switch and electronic | 2 | Nos
regulator.
c) | Wall bracket fan point as above complete with modular type switch,plate & M.S. conceal box. Including one 2pin plug socket,front plate & conceal box at fan end. | 11 | Nos
d) | Call bell point same as as bove complete with modular type push switch,plate & M.S. conceal box with buzzer type bell. | 2 | Nos.
2 | Supply Laying of Circuite line2x2.5mmsq +1x1mmsq PVC insulated copper wire form MCB DB to l Raw power plug point (6Amps)rest are same as item no.1.3 NOS 6 amps plug connected from one circuite. | 180 | Mts
a) | Supply Fixing & connection of modular type 6 amps Plug switch complete with Ms box Socket to fixed above table. 03 nos plug can be connected from 01 circuite | 14 | No.
b) | - Do - but 16 Amps 6pin socket with 16amps switch for raw power point. ( 01 Nos plug connected from one circuite.)in cluding 2x4sqmm +1x1.5sqmm earth wire. | 9 | No.
TELEPHONE WIRING.
3 | Supply laying & connection of same as iem no.1 but with 2 pair 0.51mmsq tinned CU.conductor through PVC regid ISI mark pipefrom telephone point to Korne DB complete with RJ - 11 telephone socket modular type in MS conceal box. | 3 | No.
a) | Do - 20 pair .51mmsq copper conductor telephone cable in 20mm dia PVC pipe | 55 | Mts
b) | Supply fixing & connection of 20 pair KRONE connector DB complete with PVC moulded Telephone DB box with locking system. | 1 | Set
PARTICULAR
SL. | SUPPLY FIXING & CONNECTION
LIGHT FITTINGS / FANS :
a | Wipro make Recess mounted 2x36watt WIPRO MAKE FITTING 2'-0"X2'-0"(WVP- 25236) T-5 lamp | 18 | Nos.
b | Philips make Surface mounted TL fitting 1x40watt (TMC 501/136 HPF) Philips | 14 | Nos.
c | Wipro make Recess mounted 2x18watt LED Bajaj/ Pansonic/ Philips Make | 18 | Nos
d | Wipro make Recess mounted 1x18watt Bajaj/ Pansonic/ Philips Make | 6 | Nos
e | Philips make 2x36watt TL fitting | 4 | Nos
d | 225 mm dia heavey duty Exhust fan 230 voltA.C. ( EPC / Crompton make). | 2 | Nos.
e | Ceiling fan 1200 mm dia. | 1 | Nos
f | Wall mountaing fan 400 mm dia 230 volt A.C. | 8 | Nos.
H | Pictures Light | 4 | Nos.
UPS WIRING :
5 | Supply fixing & connection of UPS circuite line with 2x2.5+1x1.5mmsq through regid PVC conduite 20mmdia 1.6 mm wall tickness, with ISI mark, to lay from UPS MCB DB to plug point board.rest same as item no.1 Two nos point to be connected from One circuit | 155 | Mts
6 | Suppy fixing of 2x6Amps 5 pin socket + 1x16 Amps 6 pin socket in single board (under table) + 1x16 A switch in another board above table as per direction. | 12 | Set
a) | - Do - but 3x6/16, 6pin socket with switch to provide near HUB rack, are to be connected from UPS power. | 2 | Set
b) | Supply laying & connection of UPS incomming power linewith 2x6mmsq +1x2.5MMSQ PVC insulated copper wire rest same as item no item no. 1 from LDB to UPS incomming power switch.including 1 nos outgoing line. | 65 | mtr
c) | Supply installation of UPS incomming 63Amps DP MCB with orginal housing of LEGRAND make. | 2 | no
d) | Supply installation and termination of UPS outgoing power distribution system with 8+2Way SPN DB comprising 8x10Amps SP MCB & 40 Amps DP MCB as main. DB with IP-20 protection | 1 | no
6 | LAYING OF CABLE :
a) | Supply laying fixing main power with 50mm sq 3.5 core PVC insulated,PVC sheated Alu.Conductor, 1100 v. grade armoured cable complete with 02 nos 8 SWG bear GI.wire as running earth. | 45 | Mts.
b) | End termination of 50mmsq 3.5 Core armoured cable,complete with brass cable gland , Alu. Lug, PVC tape. | 2 | NOS
8 | Supplying & laying of followings 1100 V grade XLPE insulated & FRLS PVC Sheathed armoured aluminum conductor cables conforming to IS 7098 with 2x8 SWG G.I wire by G.i Bar and saddles on wall ceiling and wall/floor pass through G.I class B G.I pipe
c) | 4x25sq mm for AC/POWER D.B | 35 | Mts
d) | 4X16 SQMM FOR LIGHT D.B | 18 | Mts
9 | MAIN ELECTRICAL DISTRIBUTION
wall mouting type.
Supply, fabricating,assembling,internal- connection, testing & connceting with incomming, out going power cables & lines as required to complete the job of cubical type electrical panal made from 14SWG CRC. M.S. sheet with proper earthing terminal(Nut- bolt &washer) 02 No.outside of panal, same nut- bolt to tighten with internal earth busbar of panal situated inside loose wire box(on top portion of panel)On top side of panel cable entry arragement to be done for incomming & out going of lines. Painting powder coating electrical grey/ seimensgrey to be done.one 6"x4" enamal type 440Volt Danger board to fix up on main panal bus-bar cover, components are as follows :-All switches are front handle operated & all MCB knob should be visual, all component to provide in separate compartment only DBs in one compartment.
125 Amps FP MCCB 25KA : 01 No 160 Amps 4pole Cu. Bus Bar. 01 Set. 125 Amps 4 pole Change over switch. 01 No. 63 Amps 4 pole MCB. = 03 No. ( L.D ) (P.D.B,AC D.B ) 63 Amps (DP MCB UPS) 02 Nos. Amps Meter 0-100 Amps with 3 Nos. CT & selector switch 96x96mm 01 Set (Changeover should be ON-LOAD type.)
Volt meter 0-500volt A.C. 50 Hz.96x96mm
with selector switch. AE make.n 01 Set
20mmdia LED indicator lamp 06 Nos.
02 Amps Sliding Fuse. 06 Set.
150x100mm enamal Danger board 440 volt.
| (to set on bus bar cover). 01 No. | 1 | Set
9(a) | 4way TPN MCB DB with
63 TP&N MCB as main ( POWER DB & LIGHT D.B)
16Amps SP MCB - 6 Nos+32AMPS SP X6 NOS.
| including Neutral Bar. 01 Set | 1 | Set
9(b) | 4way TPN MCB DB with
40 TP&N MCB as main (LIGHTING DB).
16 Amps SP MCB - 03 Nos.+
10 Amps SP MCB - 09 Nos.
| Including Neutral Bar. 01 Set | 2 | Set
10 | EARTHING STATION :
a) | Earthing installation as per I.E. rule conforming
to IS 3043-1987 or its latest amendent by
making earth station with 600x600x3mm(mini-
mun) thick copper plate electrode to be installed
such that is top edge shall be at a minimum depth
of 3.3mts below ground level after preparation
of ground with charcoal, sand ,& salt, connecting
the 25x3mm thick copper lead in strip (upto 10
mts length) by bolting and brazing to the copper
plate complete with Brass bolt of suitable
length double nuts & washer including supply &
fixing of 50mm dia 2.3Mts long partly perforated
G.I. Pipe with funnel for watering arragment.
N.B :- The Copper plate to be buried under
3.3Mts depth from ground level, including
| C.I. Pit 300x300mm with necessary brick | 2 | Set
wall ( For UPS earthing).
b) | SpikeEarthing with G.I. Electode 3mts. Longx50
mm dia (Class - B) including accessories and
providing masonary enclosure with cover
300x300mm plate having locking arrangement
and watering funnel Etc. with charcoal,
sand & salt at alternate layer as required
for electrical panal earthing.
| (For main electrical panel earthing.) | 2 | No.
c) | Supply laying 2x8SWG copper bear wire from
| earth spike to main panal.(Electrolite wire) | 18 | Mts
d) | Do but with 1x16mmsq insulated
copper wire from earth spike to UPS earth
bus bar through PVC regid 20mmdia ISI
| mark. | 0 | Mts
9 | Supply 2 No 3 Core 2.5mm Insulated Copper Wire with
| 15 Amp top for Supply to strong room | 0 | Nos
11 | A/C. electrification :-
a) | Supply laying & connection of A/C. line for
1.5 /1TR A/C. window / splite with 2x6 + 1x2.5
mmsq throughRegid PVC conduite rest same
| item no 1. | 85 | Mts
b) | Supply fixing of A/C. 18-25 Amps stator
complete with 20 amps socket in modular
| type box.( Noth - West Make) | 5 | Nos
C | Supply laying of 25mmsq PVC insulated CU. Standed WIRE FLEXIABLE PIPE | 45 | Mts
12 | Out door type glow sgn board wiring :-
a) | Supply laying of main line with 2x2.5 +1x1.5 | 30 | Mts
mmsq through MS conduite from main panal
to glow sign board.
b) | Supply installation of 16 amps DP MCB at main
| entrance Glow sign board | 1 | Set
C) | Supply fixing of 125 Amps TPN HRC type SFU
| at SEB for main incomming on MS angle. | 1 | No.
frame & 02 nos Cable end box including
connection.
13 | Gen set wiring :-
a) | Supply laying fixing main power with 3.5 core
50Sq.mm PVC insulated,PVC sheathed Alu.
| Conductor, 1100 v. grade armoured cable | 0 | Mts
complete with 02 nos 8 SWG bear GI.wire
as running earth.
b) | End termination of 3.5 core50 Sq.mm | 0 | End
armoured cable,complete with brass cable
gland , Alu. Lug, PVC tape.
TOTAL
DATA WIRING / NETWORKING-
1
a | S&I of cat 6 non plenum giga speed cable (CommScope,)305 Mtrs. Each | Boxes | 6
b | S & I of 2 Port Dual modular Plate | Nos | 14
c | S & I of 4 Port Quad modular Plate | Nos
d | S & I of Information Outlet ( Blue/Green) | Nos | 10
e | S & I of cat 6 3 ft mounting cord | Nos | 16
f | S & I of cat 6 7 ft mounting cord | Nos | 14
g | S & I of cat 6 20 ft mounting cord for connecting network rack and server rack | Nos | 2
h | 24 U floor mounted Server Rack (APW - president make Cyber Rack) Black Colour, Perforated Steel Door, Fan-4 Nos.5/15 Amp. 7 Socket Power Stript Generic -1 No, 725mm Shelf -1 No.,Keyboard Tray 1 No.,Cable Manager - 1 No., Hardware Pkt -1 No. | Nos | 1
i | 24 Port Patch Panel Kit | Nos | 1
j | 24 Port Switch Comscope | Nos | 1
k | CPCFF12-03F007 Visipatch 360 Visipatch 360 XL 4 Pair Patch Cord | Nos | 10
l | CPC3312-03F015 - to be used as single ended patch cord | Nos | 10
m | Testing & Documentation | Nos | 22
n | PVC Data Outlet Surface Box | Nos | 4
o | S & I of 50 Pair riser cable | Mtrs | 2
p | S & I of Krone type 300 pair junction box | Nos | 1
Total
| TOTAL |  |  |  | 0

## AC
BOQOF AIR - CONDITIONING WORK FOR NAINITAL BANK AT TALLITAL, NAINITAL
S.NO |  | UNIT | QTY | RATE | AMOUNT
1 | Copper Refrigerant Piping :
a | Installation & commissioning of Soft copper piping with | Rmt | 80
complete fiting & insulation
2 | Drain Piping
a | Hard PVC insulated drain water piping wprk of size 25 mm | Rmt | 65
dia with complete fiting Etc.
3 | Electrical Cable
a | Providing & fixing of interconected electrical wiring between
| indoor & outdoor unit as req. complete as per design & | Rmt | 145
specification of manufacturer.
4 | Civil Work For cutting Chisling Plastering of
walls to conseal copper pipe, Drain pipe &
| Electrical wire with plaster finish. | LS | 1
5 | Providing and fixing timer switch for switching power alternatively between two A/C, timer will be analogue dial type adjustable TIMER switch which is adjustable over 24hrs. With 15 minutes intervals and is to have 1NO+1NC (20A) contact. Timer will have its own backup battery and will be enclosed in 16gauge MS Box with acrylic lid together with suitable connector block. (ABB/MDS/L&T) | No | 3
6 | Providing and fixing 1.5 Tr HWAC Machine complete set with indoor and outdoor units of Voltas /Carrier or equivalent machines as per the approved list of the Bank, | No | 3
TOTAL AMOUNT